## Slide 1: Maintenance of Fire protection system
Lim Shien Ming
7 Mar 2023
2 CPD Points

## Slide 2: Course Facilitator
Mr. Lim Shien Ming
Mobile : 96194592 Email : shienming.lim@gmail.com
Senior Fire Safety Manager for IR , Super High Rise, Nursing Home, Mixed Development, Light Industry
Qualified Workplace Safety Health Officer
Qualified CERT instructor / ACTA trainer
BEnvOSHGrad
Adjunct Lecturer, FSM course
Speaker for events hosted by SCDF / NFEC / FSMAS / CAG(AES)
Fire Rescue Coordinator for USS amusement rides
Education Chairman, Fire Safety Manager Association (Singapore)

## Slide 3
Fire Technology & relevant Singapore Standards / Code of Practise
Sprinklers CP 52
Fire Alarm / Detectors SS 645 (Former CP 10)
Emergency Voice Comms SS 546
Fire Extinguishers SS 578
Hydrants, Wet / Dry Rising Mains, Hosereels SS 575
Smoke Control Chapter 7 ( Fire Code / SS 553)

## Slide 4
Maintenance is to be carried out by System Vendor Competent Person
Testing and certification is to done by Professional Engineer

## Slide 5: Fire Detection & Alarm System
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Visual Inspections
  Functional testing of indicator panels
  Field testing of initiating devices
  Testing of Building services response to fire alarm

## Slide 6
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Visual Inspections
    Check that all equipment are of approved type
    Check locations, spacing are in accordance to approved drawings
    Check conditions of conduits trunkings and paintwork
    Check conditions of initiating devices
    Check detectors and other initiating devices are not obstructed
    Check zone chart for correct locations of initiating devises

## Slide 7
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Functional testing of main / sub alarm panels (MAP/SAP)
    Alarm-For testing alarm condition
    Normal/reset-Normal condition
    Isolate/inhibit-Isolate the detection loop from the panel
    Fault-Indicating fault condition
    Check physical condition of batteries
    Check voltage & current using a multimeter
    Check battery monitoring device by disconnecting the battery terminals (Fault buzzer & battery fault indicator)
    Check and test the charger monitoring device. ( cut off the AC supply fault buzzer will sound with fault indicator lighted)

## Slide 8
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Functional testing of main / sub alarm panels (MAP/SAP)
    Check and test the earth fault supervising device
    Earth fault could be initiated on the terminals of manual call points, alarm bell lines, and detector terminals (The fault buzzer will sound with earth fault indicator lighted)
    Check and test the working conditions of all indicator lights
    Check that the system is connected to the DECAM, and fire alarm signals are correctly transmitted to the monitoring company

## Slide 9
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Field testing of initiating devices
    Two persons required
    Monitoring activities & observations must be fed back to each other
    Test manual call points for each zone by inserting key
    Ensure alarm activated
    Ensure activated zone correctly shown in the indicator panel
    Smoke detectors.
    Introduce smoke into smoke detectors
    Ensure alarm activated & signal displayed in the fire indicator panel

## Slide 10
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Field testing of initiating devices
    Heat detectors
    Introduce heat using 100 Watt bulb or Hair dryer
    Ensure alarm initiated, signal displayed on the indicator panel
    SS 645 stipulates that the maintenance engineer should arrange to check the operation of at least 20% of the detectors in an installation each year
    The selection of detectors should be made in such a way that all detectors in an installation should have been checked once in any period of 5 years

## Slide 11
SS 645: 2019 (Installation and servicing of electrical fire alarm system)
Automatic fire detection and alarm system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 645
Testing and Maintenance of Fire Detection and Alarm System:
  Testing of building services response to fire alarm
    Homing of all lifts
    Shut down of Air Handling Unit (AHU)
    Operation of smoke extraction fans (within 60 seconds)
    Operation of pressurisation fans
    Open position of sliding doors
    Releasing of magnetic door holders

## Slide 12
Testing and Maintenance of EVC Systems
Weekly Test
Combined monthly test Fire Alarm & EVC Systems under simulated fire emergency conditions
Message transmitted over loudspeakers
Message from handset from each floor to confirm loudspeakers operating
Acknowledge from master handset
Recorded in log book

## Slide 13
Monthly Test
Check
  all visual & audible indicating devices at FCC
  all controls, alarm signal silencing & alarm
  signal transferring devices
  alarm sounding devices throughout building using control at FCC
  loudspeakers by actuating selectively & collectively from FCC
  handsets by transmitting calls
  building service facilities controlled from FCC
  recording system working

## Slide 14: Sprinkler System
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Visual Inspections
  Water proving test
  Testing of sprinkler pumps
  Testing of sprinkler alarms
  Checking of water supply

## Slide 15
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Components of a wet sprinkler system
  Two pressure gauges
  Pressure switch
  Retard chamber
  Alarm gong
Operation of wet sprinkler system
Integrated alarms in sprinkler systems

## Slide 16
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Visual Inspections
  Sprinkler heads not obstructed/not painted over
  No dust collection on sprinkler heads (industrial environments)
  Corrosive vapours settling (industries)
  Protective guards provided to sprinkler heads (loading & unloading areas)
  System pressure & Supply pressure are almost equal.
  Sprinkler stop valve in fully open position
  Sprinkler drain valve & test valves are in fully closed position
  Alarm motor and gong is secured fully open

## Slide 17
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Visual Inspections
    Pumps in auto mode.
    Sprinkler risers to indicate stories served.
    Breeching inlet rigidly supported and housed in protective enclosure

## Slide 18
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Water proving test
    Objectives of the water proving test are to determine :
    Design flow rate achievable
    Running pressure at the design flow rate
    Professional Engineer (PE)/Qualified Person (QP) /Registered Inspectors (RI)
      Is required to witness the water proving test and authenticate the performance

## Slide 19
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Testing of sprinkler pumps
    Arrangement of pumps for sprinkler system
      One electric pump (duty) and one diesel pump (stand by); or
      Two electric pumps one serving as duty and the other stand by of similar capacity, both connected to generator power supply
    Check all pump suction and delivery valves are fully opened.
    Check sensitivity of the jockey pump.
    Cut-in cut-out pressure for the jockey pump.
    Sprinkler pump starting at the pre-set pressure.
    Check pump alarm indicator

## Slide 20
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Testing of sprinkler pumps
    Simulate failure of the duty pump and verify operation of stand be pump change-over mechanism
    Run pump under full load for 10 minutes (NFPA) recommendation
    Check for excessive noise & vibration of each pump and motor during operation
    Conduct visual inspection for all glands, seals and pipeline connections to ensure no leakage
    Check priming arrangements
    Check alignments & coupling between the pumps
    Check pumps can be stopped manually
    Diesel pump if installed the problems are usually confined to the starting mechanism:
      Check engine oil, water level before starting the pump
      Start the pump and let it run on full load for 30 minutes. (NFPA recommendation)

## Slide 21
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Testing of sprinkler pumps
    Check battery charging equipment, and voltage.
    Check battery test switch.
    Ensure terminals are clean and secure, top up battery electrolyte level if necessary
    Check pump control panel
      Check performance of fire pump control panel for automatic & manual operations
      Conduct visual inspection for conditions of all electronic components : resisters , capacitors & cables.
      Ensure electrical cables and terminals are secured and tightened
      Ensure all indicator lights and buzzer for correct operations
      Check for panel corrosion

## Slide 22
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Testing of sprinkler pumps

## Slide 23
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Testing of sprinkler alarms
  Check and verify operation of all water flow equipment
    Water flow gong
    Pressure switches
    Flow switches
  Clean strainer on alarm motor in the gong
  Check for general sounding of fire alarms

## Slide 24
CP 52:2004 (Automatic fire sprinkler system)
Automatic fire sprinkler system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of CP 52
Testing and Maintenance of Automatic Fire Sprinkler System:
  Checking of water supply
    Verify suction delivery and balancing valves from tank is secured fully open, strapped and padlocked
    Check for water level indicator & physical water level in the tank.
    Check for tank filling mechanism: PUB supply, transfer tank, transfer pumps
    Water tank capacity in order

## Slide 25
Wet Rising Main
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Visual Inspections
  Flow test
  Static pressure test
  Testing of pumping equipment
  Water supply & storage
25
Wet riser systems are used for buildings with habitable storey above 60m in habitable high
Wet risers are built in facility for SCDF personal to use in the event of an out break of a fire in a high-rise building

## Slide 26
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Visual Inspections
  Breeching inlet:
    Clear of obstructions
    Housed in protective enclosure & rigidly supported
    Painted red and labelled “Wet riser breeching inlet”
    Stack numerically differentiated

## Slide 27
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Visual Inspections
  Breeching inlet:
    Breeching inlet connected to wet riser water tank or transfer tank
    Location of breeching inlets are according to plan

## Slide 28
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Visual Inspections
  Riser pipes:
    Number of riser stacks in order
    Direction of flow indicated
    Earthling provided
    Fire rated cover for pipe sections passing through unprotected areas
    Air release valve provided

## Slide 29
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Visual Inspections
  Landing Valves:
    Conditions of hand wheel satisfactory
    Strapped & padlocked
    Pressure reducing facility provided if applicable
    Riser numbers clearly indicated
    Clear of obstructions
    Painted in red

## Slide 30
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Flow test
  The wet riser system are tested for sufficient discharge flow under gravity feed or pump operation
  The minimum discharge stipulated in the SS 575 as follows:
    Commercial buildings – 38 litre/s
    Residential buildings – 27 litre/s

## Slide 31
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Flow test
  The procedure is first hydraulically critical landing valve must be identified. Usually the highest or lowest landing valve in the riser stack is subjected to flow test.

## Slide 32
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Flow test
  A hydrant flow testing nozzle is connected to the landing valve and the flow is measured

## Slide 33
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Flow test
  The code of practice also permits testing wet riser system by opening three landing valves concurrently and measuring the cumulative flow
  The average cumulative flow should be greater than 38 l/s.

## Slide 34
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Static pressure test
    Identify hydraulically critical landing valves for static pressure.
    The maximum static pressure at the critical landing valves should not exceed 8 bars
    Static pressure could be measured by pressure gauge which can be fixed on the landing valves

## Slide 35
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Wet Rising Main:
  Testing of pumping equipment is similar to sprinkler system
  Water supply & storage checking procedures are similar to sprinkler system

## Slide 36: Dry Rising Main
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Dry Rising Main:
  Visual Inspections
  Hydrostatic Pressure Testing
36
Dry riser systems are used for buildings with habitable storey above 10m to 60m in habitable high
Dry risers are built in facility for SCDF personal to use in the event of an out break of a fire in a high-rise building

## Slide 37
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Dry Rising Main:
  Visual Inspections
    Breeching inlet
    Riser pipe
    Landing valves
    Inspections are similar to wet rising mains system

## Slide 38
SS 575:2012 (Fire hydrant, rising mains and hose reel systems)
Rising mains must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 575
Testing and Maintenance of Dry Rising Main:
  Hydrostatic Pressure Testing:
    Charge the rise stack with water using a hand pump or a motorised pump and develop a pressure of 200psi or 14 bar and lock the valve so that you will be able to observe any pressure drop
    The pressure must remain unchanged for 2 hours

## Slide 39: Smoke Control System
SS 553 (Mechanical ventilation and air-conditioning in building)
Mechanical ventilation system must be regularly inspected and tested to satisfactory standard in accordance with the requirements of SS 553
Staircase Pressurisation System
  Check the pressurisation system automatically activated upon the activation of the fire alarm
  Fans operate at higher speed if two-speed system is installed
  Fans operate immediately if single speed system is installed
  Check fans are capable of operating under PUB power & secondary power supply
  Check Average air flow across doors when any two consecutive storey and the main exit door are opened simultaneously opened should not be less than 1m/s

## Slide 40
Staircase Pressurisation System
  Check air pressure not less than 50 pa
  Check air pressure not to exceed 60 pa
  Check force required to open any door should not exceed 110 Newtons
  Check fans can be stopped manually

## Slide 41
Smoke Control System
  Check smoke extraction fans operate with the activation of fire alarm.
  Check external open doors used as replacement air ( doors open automatically)
  Smoke curtains if installed should lower with the activation of the fire alarm
  Check smoke extraction system connected to PUB & Secondary power supply, & able to operate under PUB and secondary power supply.
  Check smoke extraction fans start and stopped manually

## Slide 42: Summary

## Slide 43
Maintenance is to be carried out by System Vendor Competent Person
Testing and certification is to done by Professional Engineer

## Slide 44: Thank you
Lim Shien Ming
Association of Strata Managers
www.asm.org.sg
Email: secretariat@asm.org.sg